J31

Liquid applied waterproof roof coatings

Euroroof Impermax - Warm roof covering on WBP Plywood

NEW BUILD

All clauses with the suffix ‘A’ are either NBS Plus non-standard clauses and/or amended by Alumasc.

J31		LIQUID APPLIED WATERPROOF ROOF COATINGS

To be read in conjunction with related Architectural Sections, Preliminaries and Contract Conditions.

TYPES OF COVERING

102-A	ROOF COVERING OVERVIEW

- Euroroof Contact Adhesive.

- Euroroof Self-Adhesive Vapour Barrier Plus.

- Euroroof PU Insulation Adhesive.

- ___mm Alumasc GTF Rigid Polyisocyanurate Insulation.

- Euroroof PU Membrane Adhesive.

- Hydrogard 10 preparation layer.

- Euroroof Impermax Quick-Cure base coat.

- Euroroof RF225 glass fibre reinforcement matting.

- Euroroof Impermax Quick-Cure top coat.

120-A	 WARM DECK ROOF COATING

- Substrate: Minimum 18mm WBP exterior grade plywood to structural engineer's/architect's specification.

- Fixed using corrosion-resistant screws or ring shank nails, in accordance with DD CEN/TS 12872.

- Expansion gap of one millimetre per metre of the panel size should be provided at all edges.

- Falls: Roof falls are to be designed within the structure to achieve a minimum finished fall of 1:80.

- Preparation:

- Surface is to be dry, clean and free from all contaminants including oils, grease, dirt and debris.

- Tape joints with 150mm wide strips of bituminous membrane.

Attachment: As clause 616-A.

•	Primer: Euroroof Contact Adhesive.

Application: As clause 720-A.

•	Vapour control layer: Euroroof Self-Adhesive Vapour Barrier Plus.

Attachment: Self-adhered including overlaps, as clause 630-A.

•	Insulation:	- Field ___mm Alumasc GTF Rigid Polyisocyanurate.

Attachment: Partially bonded by Euroroof PU Insulation Adhesive, as clause 640-A.

- Carrier membrane: Hydrogard 10.

Attachment: Bonded in Euroroof PU Membrane Adhesive, as clause 730-A.

- Waterproof coating: Euroroof Impermax Cold-Applied Liquid Roofing.

- Manufacturer:	Alumasc Exterior Building Products Ltd

White House Works, Bold Road

Sutton, St Helens, WA9 4JG

Telephone: 01744 648400

Email: waterproofing@alumasc-exteriors.co.uk

- Primer to detailing: Subject to substrate, refer to clause 353-01.

Application: As clause 720-A.

- Base coat: Euroroof Impermax QC Black.

Application: Apply by roller/or brush at a minimum coverage rate of 1.0-1.25 litres/m², as clause 760-A.

- Reinforcement/s: Euroroof RF225.

Application: Embedded into the wet Impermax base coat, as clause 760-A.

- Top coat: Euroroof Impermax QC Dark Grey.

Application: Apply by roller/or brush at a minimum coverage rate of 0.75-1.0 litre/m², as clause 760-A.

- Protective coat/walkways: Euroroof Colodur. Optional, delete as appropriate inc. clauses 353-08, 761-A.

Colour: Select from Transparent / RAL colour as specified by the appointed design professional.

Application: Apply by roller/or brush at a minimum coverage rate of 300g/m², as clause 761-A.

•	Accessories:	Alumasc Harmer outlet/s, see clause 392-A.

Alumasc A Range modular rooflight/s, see clause 393-A.

Alumasc Toptrim GRP prefabricated edge trim, see clause 355.

PERFORMANCE

202		CONTRACTOR’S DESIGN OF ROOF COVERINGS

- Design responsibility: ______ .

- Structural and fire requirements:

- Generally: As section B50.

- Modifications: ______ .

- Design: Complete the design in accordance with the designated code of practice to satisfy specified 			  performance criteria.

- Functional requirements:

- Performance: ______ .

- Additional requirements: ______ .

- Design and production information: ______ .

- Timing of submissions: ______ .

205		COMPLETION OF DESIGN OF ROOF COVERINGS

- Description: ______ .

- Requirement: Complete the detailed design to satisfy specified performance criteria and coordinate with the detailed design of related and adjacent work.

- Structural requirements: As section B50.

- Additional requirements: ______ .

- Design and production information: ______ .

- Timing of submissions: ______ .

207		ROOF COVERING DESIGN PROVIDED

- Description: ______ .

- Requirements:

- Generally: As section B50.

- Additional requirements: ______ .

210	ROOF PERFORMANCE

- General: Secure, free draining and weathertight.

Select from either, clause 220, or alternatively, clause 225, delete as appropriate.

220		AVOID OF INTERSTITIAL CONDENSATION: WARM AND INVERTED ROOFS

- Interstitial condensation risk of roof: Determine as recommended in BS 6229.

- Basic design data:

- Outdoor notional psychrometric conditions, winter:

Temperature: - 5°C.

Relative humidity: 90%.

Vapour pressure: 0.36 kPa.

Duration: 60 days.

- Outdoor notional psychrometric conditions, summer:

Temperature: 18°C.

Relative humidity: 65%.

Vapour pressure: 1.34 kPa.

Duration: 60 days.

- Indoor notional psychrometric conditions:

Temperature: ______ ºC.

Relative humidity: ______ %.

Vapour pressure: ______ kPa.

- Winter interstitial condensate:

Calculated amount (maximum): 0.35 kg/m².

Calculated annual net retention: Nil.

- Vapour control layer: If necessary, provide a suitable membrane so that damage and nuisance from interstitial condensation do not occur.

225		AVOIDANCE OF INTERSTITIAL CONDENSATION: WARM AND INVERTED ROOFS

- Determine: Interstitial condensation risk of roof construction as recommended in BS 5250.

- Vapour control layer: If necessary, provide a suitable membrane so that damage and nuisance from interstitial condensation do not occur.

230-A	INSULATION

- Requirement: Determine type and thickness of insulation and integral or separate overlay to satisfy the following criteria:

Thermal transmittance of roof (maximum): ______ W/m² k.

- Compressive strength of insulation (minimum) at 10% compression: 150 kN/m².

Compressive creep to EN 1606: 40 kN/m² recommended design load.

- Finished surface: Suitably even, stable and robust to receive the covering.

- Insulation compliance: To relevant British Standard, or Agrément certified.

280-A	GENERAL DESIGN REQUIREMENTS

- All works must comply with all current relevant standards, codes of practice, and the Building Regulations to provide a secure, free draining and completely weathertight roof, including but not limited to:

- BS 6229 - Flat roofs with continuously supported coverings. Code of practice.

- BS 5250 - Code of practice for control of condensation in buildings.

- BS EN 1991-1-4 Eurocode 1 - Actions on structures. General actions. Wind actions.

- BS EN 12056-3 - Gravity drainage systems inside buildings. Roof drainage, layout and 	calculation.

- BS EN ISO 6946 - Building components and building elements. Thermal resistance and thermal 				  transmittance. Calculation method.

- The Building Regulations Approved Document Part L1 or Part L2. Conservation of fuel and power.

- The design must take account of all structural factors to ensure that the waterproof covering is able to accommodate the effect of movement in order to avoid stress or deformation under these conditions.

- The waterproofing components' resistance to dead and imposed loading must be assessed to avoid failure of the component/and or reduction in performance. Where resistance is deemed to be inadequate, suitable measures to mitigate load intensity will need to be considered.

- Insulation must be incorporated to avoid cold bridges as determined by building control and/or appointed design professional.

- The design must ensure that the continuity of the waterproof covering is maintained for a vertical height of at least 150mm above the finished roof level at all abutments, parapets etc.

- The building owner or their appointed design professional must have satisfied themselves that the roof structure and deck are suitable to receive the dead load of the proposed specification.

- It is strictly the responsibility of the client and/or their design professional to ensure compliance of the proposed specification with all relevant Building Regulations by consultation with Building Control. In the event of any doubt about the interpretation or application of the Building Regulations in relation to any particular new build or refurbishment works, clarification must be sought directly from Building Control.

PRODUCTS

301-A	PRIMER

- Type: Contact adhesive.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Euroroof Contact Adhesive.

- Packaging: 17 kg Canister.

- Approx. coverage (maximum): 17 kg = 270m².

- Storage temperature: +16ºC, keep clear of the ground.

305-A	BONDING COMPOUND - INSULATION

- Type: High foaming one part polyurethane adhesive.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Euroroof PU Insulation Adhesive.

- Packaging: 6 kg Cans or 17 kg Canister (17 kg Canister requires a wand applicator, hose and cleaning kit).

- Approx. coverage: 6 kg = 30-40m² to central areas & 20-30m² at perimeter & exposed areas.

17 kg = 350m² to central areas & 250m² at perimeter & exposed areas.

- Storage temperature: +10ºC, keep clear of the ground.

306-A	BONDING COMPOUND - CARRIER MEMBRANE

- Type: Low foaming one part polyurethane adhesive.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Euroroof PU Membrane Adhesive.

- Packaging: 6 kg Cans or 17 kg Canister (17 kg Canister requires a wand applicator, hose and cleaning kit).

- Approx. coverage: 6 kg = 30-40m² to central areas & 20-30m² at perimeter & exposed areas.

17 kg = 250m² to central areas & 170m² at perimeter & exposed areas.

- Storage temperature: +10ºC, keep clear of the ground.

307-A	COVER STRIPS TO JOINTS IN RIGID BOARD SUBSTRATES

- Bitumen membrane: To BS 8747 class S2P3.

- Width: 150mm.

315		TIMBER TRIMS, etc.

- Quality: Planed. Free from wane, pitch pockets, decay and insect attack (except ambrosia beetle damage).

- Moisture content at time of covering (maximum): 22%.

- Preservative treatment: To BWPDA commodity specification C8.

330-A	VAPOUR CONTROL LAYER

- Type: Glass fibre reinforced, self-adhesive, modified bitumen vapour barrier, with an aluminium core.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Euroroof Self-Adhesive Vapour Barrier Plus.

- Performance data:	Tensile Strength - Longitudinal >545 N/50mm, Transverse >387 N/50mm,

Foil thickness 20 microns.

- Roll size: Width 1m x 20m Length, Thickness 1.5mm.

333-A	RIGID URETHANE FOAM WARM DECK ROOF INSULATION

•	Standard: Polyisocyanurate (PIR) roofboard manufactured to BS EN 13165.

•	Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Alumasc GTF Rigid Polyisocyanurate.

•	Grade: 32 kg/m³.

•	Edges: Square.

- Board size: Standard 1200mm x 600mm.

•	Thickness: ___mm.

•	Facing: Mineral coated glass fibre tissue to both sides.

- Environmental status: Blowing agent: Pentane, CFC and HCFC free.

Ozone depletion potential: Zero, Global warming potential: <5.

BRE Green Guide Rating: A.

352-A	CARRIER MEMBRANE

- Type: Glass reinforced oxidised bitumen membrane.

- Product reference: Hydrogard 10.

- Performance data:	Tensile Strength - Longitudinal >266 N/50mm, Transverse >185 N/50mm,

Elongation at break (L) 3%, Softening point 80°C.

Roll size: Width 1m x 20m Length, Thickness 2mm.

353-A	WATERPROOF COATING

- Type: Elastomeric cold-applied liquid polyurethane waterproofing system with integral reinforcement.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- System reference: Euroroof Impermax Cold-Applied Liquid Roofing.

- Certification: BBA certified.

353-01	DETAILING PRIMER

- Type: Water based two-part epoxy used to seal porous substrates such as timber, concrete etc.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Humidity Primer.

- Cure time: 5-24 hours approximately, subject to ambient conditions.

- IH accelerant can be used to reduce the cure time to approx. 2-3 hours, subject to ambient conditions.

- Packaging: 5, 10 & 20 kg tins.

- Approx. coverage per coat (minimum): 0.3-0.5 kg/m².

DETAILING PRIMER

- Type: PU primer for non-porous substrates such a metal, PVC etc.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: PU Primer.

- Cure time: 2 hours approximately, subject to ambient conditions.

- IH accelerant can be used to reduce the cure time to approx. 2-3 hours, subject to ambient conditions.

- Packaging: 4, 9 & 20 kg tins.

- Approx. coverage per coat (minimum): 0.1-0.2 kg/m².

353-05	BASE COAT

- Type: Elastomeric cold-applied liquid polyurethane coating.

Colour: Black.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Euroroof Impermax QC Black.

- Cure time: 1-5 hours approximately, subject to ambient conditions.

- Packaging: 15 litre drum.

353-06	REINFORCEMENT

- Type: Glass fibre matting.

- Product reference: Euroroof RF225.

- Density: 225g/m².

- Roll size: Width 1m x 100m Length, Thickness <1mm.

353-07	TOP COAT

- Type: Elastomeric cold-applied liquid polyurethane coating.

Colour: Dark Grey.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Euroroof Impermax QC Dark Grey.

- Cure time: 1-5 hours approximately, subject to ambient conditions.

- Packaging: 15 litre drum.

353-08	PROTECTIVE COAT

- Type: 100% aliphatic cold-applied polyurethane protective top coat.

- Quartz sand or coloured granules can be incorporated to form a non-slip finish.

Colour: Select from Transparent / RAL colour as specified by the appointed design professional.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Euroroof Colodur.

- Cure time: 24 hours approximately, subject to ambient conditions.

- Packaging: 4, 9 & 20 kg tins.

355		PERIMETER TRIMS

- Type: GRP - Pultruded glass fibre reinforced polyester resin.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Toptrim.

- Colour: Select from Grey / Anthracite / Ivory.

- Size: Depth of profile Select from 40mm / 65mm / 100mm / 150mm.

- Lengths (maximum): 3m.

392-A	ROOF OUTLETS

- Type: Aluminium.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: Harmer ________.

- Size: Select from 50mm / 75mm / 100mm / 150mm.

- Accessories: Select from N/A / Screw Thread Adaptor / Flat Grate / Terrace Grate / Extension Piece.

- Product reference: Select from N/A / 2ADP (50mm) / 3ADP (75mm) / 4ADP (100mm) / 6ADP (150mm).

393-A	ROOFLIGHTS

- Type: Aluminium reinforced rigid PVC-U.

- Manufacturer: Alumasc Exterior Building Products Ltd.

- Product reference: A Range.

- Size: ___x___ mm.

•	Glazing: Select from Single skin / Double skin / Triple skin / Quad skin / Eco multiwall.

•	Shape: Select from Square / Rectangular / Circular / Pyramid / Trapezoidal.

•	Light transmission: Select from Clear / Opal diffused / Bronze / Heat Reflect.

•	Ventilation: Select from Permanent trickle / Controllable trickle / Controllable rotating /

Hinged manual 	spindle opening / Hinged electric actuator opening / Powered ventilation.

- Curb: Select from PVC-u kerb / Kerb adaptor.

- Additional features: ________ .

- Certification: BBA certified, manufactured to ISO 9001, CE mark to EN 1873.

EXECUTION GENERALLY

410		ADVERSE WEATHER

- Do not apply coatings:

- In wet conditions or at temperatures below 5°C, unless otherwise permitted by coating manufacturer.

- In high winds (speeds >7 m/s), unless adequate temporary windbreaks are erected adjacent to working 		  area.

- Rainfall: Stop work immediately, work should not be resume until the surface is completely dry.

- A curing membrane subject to rainfall can cause pits in the membrane. Where applicable, these areas 			  should be topped off accordingly to satisfy the aesthetics of the system.

- Unfinished areas of roof: Keep dry.

411-A	INCOMPLETE WORK

- Progress of the works will be such as to maintain the waterproof integrity of the roof/s. A temporary waterproofing seal is required in accordance with current codes of practice to protect the insulation.

420-A	SUITABILITY OF SUBSTRATES

- Suitability of base: Ensure that the structural tolerances of the structure which the works are being installed, are within permissible deviation of a level surface and satisfactory to receive the proposed specification. The structure is to be even and free from any irregularities that may compromise the works/and or performance. It is the responsibility of the appointed contractor to verify and report any deficiencies so that they can be corrected prior to commencing with the application.

- Substrates generally:

- Secure, clean, dry, smooth, free from frost, contaminants, loose material, voids, protrusions and organic 	  growths.

- Any imperfections or damage to existing substrates, upstands etc which are to receive new waterproofing

must be made good with suitable repair materials prior to further treatment.

- Preliminary work: Complete including:

- Formation of upstands, kerbs, box gutters, sumps, grooves, chases, and expansion joints.

- Fixing of battens, anchoring plugs/strips.

- Moisture content and stability of substrate: Must not impair roof integrity.

- Acceptable methods of drying of roof areas, where required, must be agreed with the client prior to the

commencement of works.

462-A	GENERAL NOTES / REQUIREMENTS

- Prior to installation, the Alumasc project specification, associated drawings, and manufacturer's installation instructions for all materials should have been studied and understood, and must be followed.

- These proposals relate to the roof waterproofing area only. They do not include associated work to be carried out by other trades, which may be required to complete a satisfactory refurbishment.

- All preliminary work including alterations to detailing, where applicable, is complete and satisfactory.

- Installation may only be carried out by Alumasc approved operatives, who have sufficient training for each specialist system and awareness to work safely, under the direction of qualified supervisors.

- Where applicable, all operatives must be able to produce their individual ID card upon demand, whilst installing the system for which they are approved. These should be available for inspection at all times.

- Contractor's are advised to visit site when deemed necessary and make themselves fully acquainted with the extent of the works and the conditions under which they are to be executed.

- It is the sole responsibility of the contractor to ensure that all roofing works shall be installed in accordance with the appropriate sections of all current relevant codes of practice, Building Regulations, and manufacturer's installation instructions for product supplied by the company.

- Outlet/s shall be set at a level to compensate for the thickness of the outlet flange and avoid any check against the flow of water. All outlets are to include a clamping ring to secure the waterproof covering.

- Outlets and apertures must be protected from ingress of debris to prevent blockage of downpipe/s; protection should be removed during non-operating periods.

- Where applicable, all roof services and plant, access walkways, platforms, pipes etc must be mounted on appropriate support systems providing at least 500mm clearance above the roof membrane, in order to facilitate access for future inspection/maintenance or repair.

- When applying the Euroroof Impermax waterproofing system under typical conditions, the movement of free air across the substrate will result in a rapid dispersion of vapours. However, to avoid any odours entering buildings, windows should be closed and air conditioning units switched off or redirected.

- The contractor must ensure that satisfactory aesthetic appearance of the completed works is achieved.

- On completion of the waterproofing works, check the finish for pinholes, voids, damages etc. and spot 			  treat to rectify.

463-A	SITE INSPECTIONS

- Site inspections will be made by Alumasc during the works to ensure that the installation is executed in accordance with the Alumasc warranty requirements and current codes of practice. A site visit report form, along with supporting photographs will be issued to the client/contractor following each inspection. The reports will identify and monitor the works observed during the inspections and will, where applicable, make recommendations for appropriate rectification which the contractor is to undertake in order to satisfy the warranty requirements.

464-A	HEALTH & SAFETY

- It is strictly the contractor’s responsibility to ensure that all works are executed in accordance with current health and safety legislation. Guidance may be taken from HSE publication reference: HSG33 - Health and Safety in Roof Work.

- Safety scaffolding, the location of rubbish skips, access ladders etc. should be agreed with the

client/principal contractor and be in accordance with current Health and Safety regulations.

- Product data and MSDS documents are available for all relevant products supplied by Alumasc; available for download from http://www.alumascwaterproofing.co.uk.

466-A	STORING OF MATERIALS

- Materials must be stored carefully on a clean dry and preferably warm environment. Installation equipment should also be treated in the same manner.

- Insulation should be stored inside wherever possible. If outside storage is unavoidable, the insulation 			  packaging alone under any circumstances is to be relied upon to provide sufficient protection.

- Roll materials must be stored on end.

- The load-bearing capacity of the structure must be checked if material is to be stored at roof level.

- Only sufficient material for the day's schedule should be taken out of store, or uncovered, and placed close to the area being worked. Insulation should only be unwrapped immediately prior to use.

VAPOUR CONTROL LAYERS/ WARM DECK ROOF INSULATION

616-A	JOINTS IN RIGID BOARD SUBSTRATES

- Cover strip: Lay centrally over substrate joints before laying vapour control layers or coverings. Adhere to substrate with bonding compound along edges only, or alternatively, retain in place using clout nails.

630-A	LAYING VAPOUR CONTROL LAYER

- Preparation: Substrate/s must be even and free from any irregularities that may compromise the bond.

- Bond: Full over whole surface, with no air pockets.

- Application: Remove release film and firmly pressure roll the surface and overlaps to ensure adhesion. The roll must be accurately aligned prior to the removal of the release film. Application of the insulation board is to be carried out within one week of laying the vapour control.

- Side and end laps: 75mm side lap & 100mm end lap.

- Edges of insulation at roof edges, abutments, upstands, kerbs, penetrations and the like:

- Dress to form edge protection and provide a minimum 50mm seal above the top surface of the insulation.

- Where insulation is to be installed vertically against abutments, parapets etc, the vapour control layer 	 	  	  is to be taken the full height of the insulation.

640-A	LAYING WARM DECK ROOF INSULATION

- Setting out:

- Long edges: Fully supported.

- End edges: Fully supported.

- Joints: Butt together.

- End joints: Stagger.

- Bedding: Bonded at a rate of 4No.10mm diameter beads per board width (across the board width) in central areas, and 6No. 10mm diameter beads per board width, at perimeter, detail and exposed areas.

Firmly press the insulation into place to ensure full contact and adhesion.

- Minimum application temperature of PU adhesive: 5ºC.

- Protection to exposed edges of insulation: Install treated timber batten approx. 10mm less in thickness to

the adjacent insulation, to avoid creating a step in the waterproofing.

- Completion: Boards must be in good condition, well fitting and stable.

660-A	FIXING PERIMETER TRIMS

- Setting out: 3mm (minimum) clear from wall or fascia. All lengths should be close butt jointed, using the connecting pieces supplied.

- Fasteners: Screw fixings only, type and length appropriate to substrate.

- Fixing: 30mm from ends and at 300mm (maximum) centres.

- Corner pieces: Purpose made.

- Completion:

- Contact surfaces: Prime.

ROOF COATING SYSTEM

710-A	ADHESION TESTS

- Requirement: Carry out a trial coating to determine priming requirements and/ or system suitability.

- Test results: Submit and arrange for inspection.

720-A	APPLYING PRIMERS/CONDITIONERS

- Product reference: Euroroof Contact Adhesive.

- Surface coverage: Even and full.

- Application: Liberally apply a well-distributed layer of adhesive by spray gun, do not allow the adhesive to build up at any one spot. A single layer is generally sufficient for most surfaces, depending on the degree of porosity of the base material. In view of the porosity of materials such as plywood, apply two layers of adhesive allowing the first layer approx. five minutes (dry to touch) before applying the second layer.

- Vapour control layer must be bonded within two minutes of application.

APPLYING PRIMERS/CONDITIONERS

- Product reference: Subject to substrate, refer to clause 353-01.

- Coverage per coat (minimum): Refer to clause 353-01.

- Surface coverage: Brushed well in to ensure local or full area coverage according to type.

- Coats: Allow to dry completely before overcoating.

730-A	LAYING CARRIER MEMBRANE

- Setting out: Neat, with carefully formed junctions.

- Bonding compound: Apply a 10mm diameter bead at a rate of 150g/m² in central areas and 200g/m² at perimeter and detail areas. Avoid excessive build-up of adhesive.

- Minimum application temperature of PU adhesive: 5ºC.

- Side and end laps: 75mm side lap & 100mm end lap, ensure laps are kept free of adhesive.

- Head and side laps: Offset.

- Successive layers: Apply immediately. Do not trap moisture.

760-A	APPLICATION OF ROOF COATINGS

- Final cleaning: Prior to application, ensure that all surfaces are free from visible dampness and that any surface dust, dirt and any other forms of contaminant are removed.

- Application:

- Thoroughly mix Impermax QC base using a paddle mixer at a low rpm. Ensure the product is completely 	  homogenous and then leave to rest to let excess air disperse before application. Using a roller or brush

apply at a coverage rate of 1.0-1.25 l/m². Allow to fully cure before applying Impermax QC top coat.

- Lay RF225 glass reinforcement mat immediately into the wet base coat, with 50mm side and end laps.

- Pressure roll until mat is completely embedded and thoroughly saturated.

- Once cured, inspect for any wicks or pinholes and, if required, rectify prior to applying the top coat.

- Thoroughly mix Impermax QC top coat using a paddle mixer at a low rpm. Ensure the product is 			  completely homogenous and then leave to rest to let excess air disperse before application. Using a roller 	  or brush apply at a coverage rate of 0.75-1.0 l/m².

- Coverage: Where applicable, on rough or undulating substrates, apply up to a maximum of 1.25 l/m² of Impermax Base Coat to ensure full saturation of the fibreglass matting.

- Exposure of base coat >14 days: Apply reactivation Primer at 100g/m2.

- Continuity: Maintain full thickness of coatings around angles, junctions and features.

- Rainwater outlets: Form with watertight joints.

- Drainage systems: Do not allow liquid coatings to enter piped rainwater or foul systems.

761-A	APPLICATION OF PROTECTIVE COATINGS/WALKWAY

- Setting out: Mark out using appropriate tapes to designate walkway.

- Application: Thoroughly mix Euroroof Colodur using a paddle mixer at a low rpm. Ensure the product is completely homogenous and then leave to rest to let excess air disperse before application. Using a roller or brush apply at a coverage rate of 300g/m².

- Exposure of top coat >14 days: Apply reactivation Primer at 100g/m2.

- Continuity: Maintain full thickness of coating around junctions and features.

770-A	SKIRTINGS AND UPSTANDS / GENERAL DETAILING

- Preparation: Prepare the substrate to provide an acceptable base for waterproofing.

- Prime substrate with the appropriate primer, refer to product clause 353-01.

- Reinforcement strip: Where minor movement is anticipated, loose lay a strip of Euroroof Geomax fleece immediately into the wet base coat. Pressure roll until completely embedded and thoroughly saturated. Where applicable, consult with Alumasc technical services prior to works commencing.

- Flashings and detail work:

- The design should ensure that the continuity of the waterproof covering is maintained for a vertical height 	  of 150mm above the finished roof level at all abutments, parapets etc. Alumasc cannot take responsibility 	  in the event of water ingress over and above the termination of our waterproofing.

- Leadwork: Where applicable, code 4 or 5 lead is required for flashing of details. Maximum lengths and girth should be established and carried out in accordance with the Lead Sheet Association recommendations.

- Additional requirements: The contractor is to install all details in a manner to comply with current quality assessment recommendations for the installation of the specified system. Should any detail arise where it is not clear how this can be achieved, the contractor is to seek advice and approval for all proposals from Alumasc before completing the works.

COMPLETION

910-A	FINAL INSPECTION

- Interim and final roof inspections: Strictly in accordance with Alumasc's requirements to satisfy the warranty requirements.

- Rainwater goods must be tested by the contractor upon completion of the works prior to handover.

- Alumasc will conduct a final inspection upon notification of completion by the contractor. The warranty will then be issued via the roofing contractor upon satisfactory rectification of any snags identified, or without undue delay, should all be satisfactory. Failure to instigate a final inspection may jeopardise approval and/or warranty release.

912-A	PROTECTION

- As soon as an area of  waterproofing has been completed, it should be inspected upon notification of completion by the contractor. Completed areas should not be used as a building platform or as an access route by other trades. If unavoidable, appropriate protection must be provided for the duration of the construction period. Care should be taken not to mark or dent the works while laying any additional protection. Inspection and/or leak testing must always take place after removal of such protection.

- Roofs accessed for regular maintenance of plant, or parts of the building, should be given consideration in providing a predetermined route to and from the entry point to minimise potential hazards.

940		COMPLETION

- Roof areas: Clean.

- Outlets: Clear.

- Work necessary to provide a weathertight finish: Complete.

- Storage of materials on finished surface: Not permitted.

- Completed membrane: Do not damage. Protect from chemicals, traffic and adjacent or high level working.

941-A	MANUFACTURER'S WARRANTY

- The above specification/s shall be installed in accordance with the appropriate sections of all current relevant codes of practice, Building Regulations, and manufacturer's installation instructions for product supplied by the company. The works shall only be installed by Alumasc approved operatives, and, as agreed in the contract, the Alumasc Warranty shall be issued to the building owner on satisfactory completion.

942-A	MAINTENANCE

- It is recommend that all flat roofs be inspected at a minimum frequency of twice a year. Ideally, inspections should be carried out in spring and autumn accounting for the effects of annual extremes of weather to be checked. Inspection should also be carried out following works on the roof by other trades, or following installation of new roof equipment.

- All inspections/and or maintenance actions carried out at roof level must be in full compliance with the appropriate health and safety regulations, and particularly those specifically dealing with working at height

--------------------

Alumasc standard NBS specifications are offered on the condition that the customer is responsible for 			ensuring that each specification is appropriate for its intended purpose and that conditions for its use are 			suitable. This specification may require adjustment in accordance with specific project requirements. NBS 		standard specifications are provided without any warranty offer for your examination.

Any variation to this specification (or any Alumasc standard specification) must be agreed with Alumasc 			Exterior Building Products Ltd, who will amend and reissue as a project specification, including warranty 			offer, in accordance with the agreed variation/s.

The substitution of any products (or installation by means other than those described) is strictly prohibited, 		unless agreed in writing, in advance, with Alumasc.

Alumasc Exterior Building Products Ltd will not accept any liability arising from unauthorised variations or 		un-notified changes in circumstances relating to the application or performance of Alumasc products or 			systems.